## LOD & MEA Definitions
LOD & MEA Definitions
OSU Project Name | Not for Use on Wexner Medical Center Projects
OSU Project Number
Primary A/E
Fundamental LOD Definitions (based on the BIMForum LOD Specification Version 2022)
LOD 100 The Model Element may be graphically represented in the Model with a symbol or other generic representation, but does not satisfy the requirements for LOD 200. Information related to the Model Element (e.g., cost per square foot, tonnage of HVAC, etc.) can be derived from other Model Elements.
LOD 200 The Model Element is generically and graphically represented within the Model with approximate quantity, size, shape, location, and orientation.
LOD 300 The Model Element, as designed, is graphically represented within the Model such that its quantity, size, shape, location, and orientation can be measured.
LOD 350 The Model Element, as designed, is graphically represented within the Model such that its quantity, size, shape, location, orientation, and interfaces with adjacent or dependent Model Elements can be measured.
LOD 400 The Model Element is graphically represented within the Model with detail sufficient for fabrication, assembly, and installation.
LOD 500 The Model Element is a graphic representation of an existing or as-constructed condition developed through a combination of observation, field verification, or interpolation. The level of accuracy shall be noted or attached to the Model Element.
General Notes
Model elements that have been assigned a Level of Development (LOD) represent the minimum deliverable requirement for the University. All other cells should be completed by the Design and Construct teams.
Additional project specific comments along with any additions and/or exclusions to the minimum LOD should be cited in the “Notes” column and further defined in the LOD Notes tab.
The Asset Tag column cites which UniFormat categories are required to have additional data associated with them, while Section 5.3. Non-Graphic Building Information (Asset Worksheet) of the BIM PDS outlines the required spatial and asset information to be included in the project deliverables.
Version 2024
Non-Wexner Medical Center Projects Only

## LOD Notes
LOD Notes
Note | Description
1 | Although standard wall and ceiling individual framing members are not modeled through LOD 300, any atypical framing features required for tiered ceilings, soffits, curved walls, arched ceilings, etc. should be modeled at a minimum for LOD 350 to ensure there is enough available space for the additional framing/bracing for these components.
2 | At LOD 100 Wall, Floor and Ceiling Finishes will be represented with text via a Room object.
3 | Wall, ceiling and/or floor furring along with other required sheathing/underlayments to be included with wall, ceiling and/or floor finish elements above as appropriate.
4 | The Plumbing Engineer will be responsible for defining the performance of the Fire Suppressions System as well as modeling; the location of fire service to the building, major equipment, standpipes and major piping runs in accordance with the defined LOD. Ancillary and secondary piping from the major piping runs to the sprinkler head locations to be designed and modeled by the Fire Protection Contractor in accordance with the defined LOD.
5 | These categories will be represented by typical details and notes that have been developed with text and/or 2D supplementation in addition to or in lieu of model geometry for items called defined at LOD 100.
6 | The Electrical Engineer will exclude branch wiring from this category. During Trade Coordination the Electrical Contractor will be expected to model all conduits larger than ¾”, and large groups of conduit ¾” (or less) in a particular location shall be modeled to reflect the overall space requirements.
7 | Performance specification (with supporting 2D Supplementation) to be developed at LOD 100 by the Electrical Engineer.
8 | These components are typically modeled as part of other assemblies listed in the tables above and will assume those LOD and MEA designations.
9 | Section G: Building Sitework items are typically designed and documented in two dimensional applications and are typically owned by CE but may be modeled for reference by LA or A. Any deviation from this reference model will be documented in the project specific BIM Execution Plan.
10 | This category is typically owned by the utility company and will be modeled for reference and coordinated accordingly by the EE.
11 | In addition to the defined Level of Development for this category the PE will also provide typical details and notes that have been developed with text and/or 2D supplementation.
12 | The Mechanical, Plumbing and Electrical Engineers will be responsible for modeling their respective engineering systems up to 5’ outside the building, from that point on ownership of the Model Elements will transition to the Civil Engineer.
13 | In addition to the defined Level of Development for this category the Technology Engineer will provide typical details and notes that have been developed with text and/or 2D supplementation. This will be inclusive of this category with the exception of cable trays and bundled conduits which will be modeled.
14 | Branch wiring to be excluded as Model Elements by the Design Team.
15 | If systems are pre-egineered they can be modeled at LOD 200.
16 | Although standard wall and ceiling individual framing members are not modeled, any atypical framing features required for tiered ceilings, soffits, curved walls, arched ceilings, etc. should be modeled to ensure there is enough available space for the additional framing/bracing for these components.
17 | All ducts and air handling equipment shall be modeled to the outside face dimension.
18 | All piping shall be modeled to the outside diameter of the pipe adding insulation as its own entity where applicable or the pipe insulation, whichever is greater.
19 | For telecommunication systems, at a minimum, all cable tray, wire managements hooks, conduit larger than ¾”, and communication racks and cabinets shall be modeled. Large groups of conduit ¾” (or less) in a particular location shall be modeled to reflect the overall space requirements.
20 | All components of the fire alarm system shall be modeled including all panels and devices with access zones and conduit larger than ¾”. Large groups of conduit ¾” (or less) in a particular location will be modeled to reflect the overall space requirements.
21 | Items called out in the Asset Tag and COBie Notes column are the only items in this section needing to be model to the outlined LOD.
22 | Wall protection modeling should include items such as bumper/crash rails, guard rails, corner guards and other wall protection items that protrude from the wall surface.
23 | Parking lot Appurtenances such as striping for parking shall be modeled for use in space quantification

## Asset Tagging & LOD Matrix
Asset Tagging & LOD Matrix of BIM Deliverables
Model Elements (Utilizing CSI UniFormat 2010) | Design | [7 empty] | Construct |  | Operate |  |  | Asset Tag Required (Notes)
|  |  | Project Stakeholder Document Review |  |  |  | Design Intent BIM |  | Trade Coordination BIM |  | Conformed Design Intent BIM
| LOD | MEA | LOD | MEA | LOD | MEA | LOD | MEA | LOD | MEA | LOD | MEA | LOD Notes
A Substructure
A10 Foundation
A1010 – Standard Foundations
A1010.10 – Wall Foundations | [6 empty] | 300 |  |  |  | 300 |  |  | -
A1010.30 – Column Foundations | [6 empty] | 300 |  |  |  | 300 |  |  | -
A1010.90 – Standard Foundation Supplementary Components | [13 empty] | -
A1020 – Special Foundations
A1020.10 – Driven Piles | [6 empty] | 300 |  |  |  | 300 |  |  | -
A1020.15 – Bored Piles | [6 empty] | 300 |  |  |  | 300 |  |  | -
A1020.20 – Caissons | [6 empty] | 300 |  |  |  | 300 |  |  | -
A1020.30 – Special Foundation Walls | [6 empty] | 300 |  |  |  | 300 |  |  | -
A1020.40 – Foundation Anchors | [13 empty] | -
A1020.50 – Underpinning | [13 empty] | -
A1020.60 – Raft Foundations | [13 empty] | -
A1020.70 – Pile Caps | [6 empty] | 300 |  |  |  | 300 |  |  | -
A1020.80 – Grade Beams | [6 empty] | 300 |  |  |  | 300 |  |  | -
A20 Subgrade Enclosure
A2010 – Walls for Subgrade Enclosures
A2010.10 – Subgrade Enclosure Wall Construction | [6 empty] | 300 |  |  |  | 300 |  |  | -
A2010.20 – Subgrade Enclosure Wall Interior Skin Plaster and Gypsum Board | [6 empty] | 300 |  |  |  | 300 |  |  | -
A2010.90 – Subgrade Enclosure Wall Supplementary Components | [12 empty] | 5 | -
A40 Slabs-on-Grade
A4010 – Standard Slabs-on-Grade | [6 empty] | 300 |  |  |  | 300 |  |  | -
A4020 – Structure Slabs-on-Grade | [6 empty] | 300 |  |  |  | 300 |  |  | -
A4030 – Slab Trenches | [6 empty] | 300 |  |  |  | 300 |  |  | -
A4040 – Pits and Basses | [6 empty] | 300 |  |  |  | 300 |  |  | -
A4090 – Slab-On-Grade Supplementary Components
A4090.10 – Perimeter Insulation | [12 empty] | 5 | -
A4090.20 – Vapor Retarder | [12 empty] | 5 | -
A4090.30 – Waterproofing | [12 empty] | 5 | -
A4090.50 – Mud Slab | [12 empty] | 5 | -
A4090.60 – Subbase Layer | [12 empty] | 5 | -
A60 Water and Gas Mitigation
A6010 – Building Subdrainage
A6010.10 – Foundation Drainage | [6 empty] | 300 |  |  |  | 300 |  |  | -
A6010.20 – Underslab Drainage | [6 empty] | 300 |  |  |  | 300 |  |  | -
A6020 – Off-Gassing Mitigation
A6020.10 – Radon Mitigation | [13 empty] | -
A6020.50 – Methane Mitigation | [13 empty] | -
A90 Substructure Related Activities
A9010 – Substructure Excavation
A9010.10 – Backfill and Compaction | [13 empty] | -
A9020 – Construction Dewatering | [13 empty] | -
A9030 – Excavation Support
A9030.10 – Anchor Tiebacks | [13 empty] | -
A9030.20 – Cofferdams | [13 empty] | -
A9030.40 – Cribbing and Walers | [13 empty] | -
A9030.60 – Ground Freezing | [13 empty] | -
A9030.70 – Slurry Walls | [13 empty] | -
A9040 – Soil Treatment | [13 empty] | -
B: Shell
B10 Superstructure
B1010 – Floor Construction
B1010.10 – Floor Structural Frame | [6 empty] | 300 |  |  |  | 300 |  |  | -
B1010.20 – Floor Decks, Slabs, and Toppings | [6 empty] | 300 |  |  |  | 300 |  |  | -
B1010.30 – Balcony Floor Construction | [6 empty] | 300 |  |  |  | 300 |  |  | -
B1010.40 – Mezzanine Floor Construction | [6 empty] | 300 |  |  |  | 300 |  |  | -
B1010.50 – Ramps | [6 empty] | 300 |  |  |  | 300 |  |  | -
B1010.90 – Floor Construction Supplementary Components | [12 empty] | 5 | -
B1020 – Roof Construction
B1020.10 – Roof Structural Frame | [6 empty] | 300 |  |  |  | 300 |  |  | -
B1020.20 – Roof Decks, Slabs, and Sheathing | [6 empty] | 300 |  |  |  | 300 |  |  | -
B1020.30 – Canopy Construction | [6 empty] | 300 |  |  |  | 300 |  |  | -
B1020.90 – Roof Construction Supplementary Components | [12 empty] | 5 | -
B1080 – Stairs
B1080.10 – Stair Construction | [6 empty] | 300 |  |  |  | 300 |  |  | -
B1080.30 – Stair Soffits | [6 empty] | 300 |  |  |  | 300 |  |  | -
B1080.50 – Stair Railings | [6 empty] | 300 |  |  |  | 300 |  |  | -
B1080.60 – Fire Escapes | [6 empty] | 300 |  |  |  | 300 |  |  | -
B1080.70 – Metal Walkways | [6 empty] | 300 |  |  |  | 300 |  |  | -
B1080.80 – Ladders | [6 empty] | 300 |  |  |  | 300 |  | 15 | -
B20 Exterior Vertical Enclosures
B2010 – Exterior Walls
B2010.10 – Exterior Wall Veneer | [6 empty] | 300 |  |  |  | 300 |  | 16 | -
B2010.20 – Exterior Wall Construction | [6 empty] | 300 |  |  |  | 300 |  | 16 | -
B2010.30 – Exterior Wall Interior Skin | [6 empty] | 300 |  |  |  | 300 |  | 16 | -
B2010.40 – Fabricated Exterior Wall Assemblies | [6 empty] | 300 |  |  |  | 300 |  | 16 | -
B2010.50 – Parapets | [6 empty] | 300 |  |  |  | 300 |  | 16 | -
B2010.60 – Equipment Screens | [6 empty] | 200 |  |  |  | 200 |  |  | -
B2010.80 – Exterior Wall Supplementary Components | [12 empty] | 5 | -
B2010.90 – Exterior Wall Opening Supplementary Components | [12 empty] | 5 | -
B2020 – Exterior Windows
B2020.10 – Exterior Operating Windows | [6 empty] | 300 |  |  |  | 300 |  |  | -
B2020.20 – Exterior Fixed Windows | [6 empty] | 300 |  |  |  | 300 |  |  | -
B2020.30 – Exterior Window Wall | [6 empty] | 300 |  |  |  | 300 |  |  | -
B2020.50 – Exterior Special Function Windows | [6 empty] | 200 |  |  |  | 200 |  |  | -
B2050 – Exterior Doors and Grilles
B2050.10 – Exterior Entrance Doors | [6 empty] | 300 |  |  |  | 300 |  |  | Y (A)
B2050.20 – Exterior Utility Doors | [6 empty] | 300 |  |  |  | 300 |  |  | Y (A)
B2050.30 – Exterior Oversize Doors | [6 empty] | 300 |  |  |  | 300 |  |  | Y (A,B)
B2050.40 – Exterior Special Function Doors | [6 empty] | 300 |  |  |  | 300 |  |  | Y (A)
B2050.60 – Exterior Grilles | [6 empty] | 200 |  |  |  | 200 |  |  | -
B2050.70 – Exterior Gates | [6 empty] | 200 |  |  |  | 200 |  |  | -
B2050.90 – Exterior Door Supplementary Components | [12 empty] | 5, 8 | -
B2070 – Exterior Louvers and Vents
B2070.10 – Exterior Louvers | [6 empty] | 300 |  |  |  | 300 |  |  | -
B2070.50 – Exterior Vents | [6 empty] | 300 |  |  |  | 300 |  |  | -
B2080 – Exterior Wall Appurtenances
B2080.10 – Exterior Fixed Grilles and Screens | [6 empty] | 200 |  |  |  | 200 |  |  | -
B2080.30 – Exterior Opening Protection Devices | [6 empty] | 200 |  |  |  | 200 |  |  | -
B2080.50 – Exterior Balcony Walls and Railings | [6 empty] | 300 |  |  |  | 300 |  |  | -
B2080.70 – Exterior Fabrications | [6 empty] | 200 |  |  |  | 200 |  |  | -
B2080.80 – Bird Control Devices | [13 empty] | -
B2090 – Exterior Wall Specialties | [6 empty] | 200 |  |  |  | 200 |  |  | -
B30 Exterior Horizontal Enclosures
B3010 – Roofing
B3010.10 – Steep Slope Roofing | [6 empty] | 300 |  |  |  | 300 |  |  | -
B3010.50 – Low-Slope Roofing | [6 empty] | 300 |  |  |  | 300 |  |  | -
B3010.70 – Canopy Roofing | [6 empty] | 300 |  |  |  | 300 |  |  | -
B3010.90 – Roofing Supplementary Components | [12 empty] | 5, 8 | -
B3020 – Roof Appurtenances
B3020.10 – Roof Accessories | [6 empty] | 300 |  |  |  | 300 |  |  | -
B3020.30 – Roof Specialties | [6 empty] | 200 |  |  |  | 200 |  |  | -
B3020.70 – Rainwater Management | [6 empty] | 200 |  |  |  | 200 |  |  | -
B3040 – Traffic Bearing Horizontal Enclosures
B3040.10 – Traffic Bearing Coatings | [13 empty] | -
B3040.30 – Horizontal Waterproofing Membrane | [12 empty] | 5, 8 | -
B3040.50 – Wear Surfaces | [6 empty] | 200 |  |  |  | 200 |  |  | -
B3040.90 – Horizontal Enclosures Supplementary Components | [12 empty] | 5, 8 | -
B3060 – Horizontal Openings
B3060.10 – Roof Windows and Skylights | [6 empty] | 200 |  |  |  | 200 |  |  | -
B3060.50 – Vents and Hatches | [6 empty] | 200 |  |  |  | 200 |  |  | -
B3060.90 – Horizontal Opening Supplementary Components | [12 empty] | 5, 8 | -
B3080 – Overhead Exterior Enclosures
B3080.10 – Exterior Ceilings | [6 empty] | 300 |  |  |  | 300 |  | 16 | -
B3080.20 – Exterior Soffits | [6 empty] | 300 |  |  |  | 300 |  | 16 | -
B3080.30 – Exterior Bulkheads | [6 empty] | 300 |  |  |  | 300 |  | 16 | -
C: Interiors
C10 Interior Construction
C1010 – Interior Partitions
C1010.10 – Interior Fixed Partitions | [6 empty] | 300 |  |  |  | 300 |  | 1, 16 | -
C1010.20 – Interior Glazed Partitions | [6 empty] | 300 |  |  |  | 300 |  |  | -
C1010.40 – Interior Demountable Partitions | [6 empty] | 200 |  |  |  | 200 |  | 16 | -
C1010.50 – Interior Operable Partitions | [6 empty] | 200 |  |  |  | 200 |  | 16 | -
C1010.70 – Interior Screens | [6 empty] | 200 |  |  |  | 200 |  |  | -
C1010.90 – Interior Partition Supplementary Components | [12 empty] | 5 | -
C1020 – Interior Windows
C1020.10 – Interior Operating Windows | [6 empty] | 300 |  |  |  | 300 |  |  | -
C1020.20 – Interior Fixed Windows | [6 empty] | 300 |  |  |  | 300 |  |  | -
C1020.50 – Interior Special Function Windows | [6 empty] | 300 |  |  |  | 300 |  |  | -
C1020.90 – Interior Window Supplementary Components | [12 empty] | 5, 8 | -
C1030 – Interior Doors
C1030.10 – Interior Swinging Doors | [6 empty] | 300 |  |  |  | 300 |  |  | Y (A)
C1030.20 – Interior Entrance Doors | [6 empty] | 300 |  |  |  | 300 |  |  | Y (A)
C1030.25 – Interior Sliding Doors | [6 empty] | 300 |  |  |  | 300 |  |  | Y (A)
C1030.30 – Interior Folding Doors | [6 empty] | 200 |  |  |  | 200 |  |  | Y (A)
C1030.40 – Interior Coiling Doors | [6 empty] | 200 |  |  |  | 200 |  |  | Y (A)
C1030.50 – Interior Panel Doors | [6 empty] | 200 |  |  |  | 200 |  |  | Y (A)
C1030.70 – Interior Special Function Doors | [6 empty] | 200 |  |  |  | 200 |  |  | Y (A)
C1030.80 – Interior Access Doors and Panels | [6 empty] | 200 |  |  |  | 200 |  |  | Y (A)
C1030.90 – Interior Door Supplementary Components | [12 empty] | 5 | -
C1040 – Interior Grilles and Gates
C1040.10 – Interior Grilles | [6 empty] | 200 |  |  |  | 200 |  |  | -
C1040.50 – Interior Gates | [6 empty] | 200 |  |  |  | 200 |  |  | -
C1060 – Raised Floor Construction
C1060.10 – Access Flooring | [6 empty] | 300 |  |  |  | 300 |  |  | -
C1060.30 – Platform/Stage Floor | [6 empty] | 300 |  |  |  | 300 |  |  | -
C1070 – Suspended Ceiling Construction
C1070.10 – Acoustical Suspended Ceilings | [6 empty] | 300 |  |  |  | 300 |  | 16 | -
C1070.20 – Suspended Plaster and Gypsum Board Ceilings | [6 empty] | 300 |  |  |  | 300 |  | 16 | -
C1070.50 – Specialty Suspended Ceilings | [6 empty] | 300 |  |  |  | 300 |  | 16 | -
C1070.70 – Special Function Suspended Ceiling | [6 empty] | 300 |  |  |  | 300 |  | 16 | -
C1070.90 – Ceiling Suspension Components | [12 empty] | 5, 8 | -
C1090 – Interior Specialties
C1090.10 – Interior Railings and Handrails | [6 empty] | 300 |  |  |  | 300 |  |  | -
C1090.15 – Interior Louvers | [6 empty] | 300 |  |  |  | 300 |  |  | -
C1090.20 – Information Specialties | [6 empty] | 200 |  |  |  | 200 |  |  | -
C1090.25 – Compartments and Cubicles | [6 empty] | 200 |  |  |  | 200 |  |  | -
C1090.30 – Service Walls | [6 empty] | 300 |  |  |  | 300 |  |  | -
C1090.35 – Wall and Door Protection | [6 empty] | 300 |  |  |  | 300 |  | 22 | -
C1090.40 – Toilet, Bath, and Laundry Accessories | [6 empty] | 300 |  |  |  | 300 |  |  | -
C1090.45 – Interior Gas Lighting | [13 empty] | -
C1090.50 – Fireplaces and Stoves | [6 empty] | 200 |  |  |  | 200 |  |  | -
C1090.60 – Safety Specialties | [6 empty] | 200 |  |  |  | 200 |  |  | -
C1090.70 – Storage Specialties | [6 empty] | 300 |  |  |  | 300 |  |  | -
C1090.90 – Other Interior Specialties | [6 empty] | 200 |  |  |  | 200 |  |  | -
C20 Interior Finishes
C2010 – Wall Finishes
C2010.10 – Tile Wall Finish | [12 empty] | 2 | -
C2010.20 – Wall Paneling | [12 empty] | 2 | -
C2010.30 – Wall Coverings | [12 empty] | 2 | -
C2010.35 – Wall Carpeting | [12 empty] | 2 | -
C2010.50 – Stone Facing | [12 empty] | 2 | -
C2010.60 – Special Wall Surfacing | [12 empty] | 2 | -
C2010.70 – Wall Painting and Coating | [12 empty] | 2 | -
C2010.80 – Acoustical Wall Treatment | [12 empty] | 2 | -
C2010.90 – Wall Finish Supplementary Components | [12 empty] | 3, 8 | -
C2020 – Interior Fabrications | [6 empty] | 200 |  |  |  | 200 |  |  | -
C2030 – Flooring
C2030.10 – Flooring Treatment | [12 empty] | 2 | -
C2030.20 – Tile Flooring | [12 empty] | 2 | -
C2030.30 – Specialty Flooring | [12 empty] | 2 | -
C2030.40 – Masonry Flooring | [12 empty] | 2 | -
C2030.45 – Wood Flooring | [12 empty] | 2 | -
C2030.50 – Resilient Flooring | [12 empty] | 2 | -
C2030.60 – Terrazzo Flooring | [12 empty] | 2 | -
C2030.70 – Fluid-Applied Flooring | [12 empty] | 2 | -
C2030.75 – Carpeting | [12 empty] | 2 | -
C2030.80 – Athletic Flooring | [12 empty] | 2 | -
C2030.85 – Entrance Flooring | [12 empty] | 2 | -
C2030.90 – Flooring Supplementary Components | [12 empty] | 3, 8 | -
C2040 – Stair Finishes
C2040.20 – Tile Stair Finish | [12 empty] | 2 | -
C2040.40 – Masonry Stair Finish | [12 empty] | 2 | -
C2040.45 – Wood Stair Finish | [12 empty] | 2 | -
C2040.50 – Resilient Stair Finish | [12 empty] | 2 | -
C2040.60 – Terrazzo Stair Finish | [12 empty] | 2 | -
C2040.75 – Carpeted Stair Finish | [12 empty] | 2 | -
C2050 – Ceiling Finishes
C2050.10 – Plaster and Gypsum Board Finish | [12 empty] | 2 | -
C2050.20 – Ceiling Paneling | [12 empty] | 2 | -
C2050.70 – Ceiling Painting and Coating | [12 empty] | 2 | -
C2050.80 – Acoustical Ceiling Treatment | [12 empty] | 2 | -
C2050.90 – Ceiling finish Supplementary Components | [12 empty] | 3, 8 | -
C2090 – Interior Finish Schedules | [12 empty] | 2 | -
D: Services
D10 Conveying
D1010 – Vertical Conveying Systems
D1010.10 – Elevators | [6 empty] | 300 |  |  |  | 300 |  |  | -
D1010.20 – Lifts | [6 empty] | 200 |  |  |  | 200 |  |  | -
D1010.30 – Escalators | [6 empty] | 300 |  |  |  | 300 |  |  | -
D1010.50 – Dumbwaiters | [6 empty] | 200 |  |  |  | 200 |  |  | -
D1010.60 – Moving Ramps | [6 empty] | 200 |  |  |  | 200 |  |  | -
D1030 – Horizontal Conveying
D1030.10 – Moving Walks | [6 empty] | 200 |  |  |  | 200 |  |  | -
D1030.30 – Turntables | [6 empty] | 200 |  |  |  | 200 |  |  | -
D1030.50 – Passenger Loading Bridges | [6 empty] | 200 |  |  |  | 200 |  |  | -
D1030.70 – People Movers | [6 empty] | 200 |  |  |  | 200 |  |  | -
D1050 – Material Handling
D1050.10 – Cranes | [6 empty] | 200 |  |  |  | 200 |  |  | Y
D1050.20 – Hoists | [6 empty] | 200 |  |  |  | 200 |  |  | -
D1050.30 – Derricks | [6 empty] | 200 |  |  |  | 200 |  |  | -
D1050.40 – Conveyors | [6 empty] | 200 |  |  |  | 200 |  |  | -
D1050.50 – Baggage Handling Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
D1050.60 – Chutes | [6 empty] | 300 |  |  |  | 300 |  |  | -
D1050.70 – Pneumatic Tube Systems | [6 empty] | 300 |  |  |  | 300 |  |  | -
D1080 – Operable Access Systems
D1080.10 – Suspended Scaffolding | [13 empty] | -
D1080.20 – Rope Climbers | [6 empty] | 200 |  |  |  | 200 |  |  | -
D1080.30 – Elevating Platforms | [6 empty] | 300 |  |  |  | 300 |  |  | -
D1080.40 – Powered Scaffolding | [13 empty] | -
D1080.50 – Building Envelope Access | [6 empty] | 200 |  |  |  | 200 |  |  | -
D20 Plumbing
D2010 – Domestic Water Distribution
D2010.10 – Facility Potable-Water Storage Tanks | [6 empty] | 300 |  |  |  | 300 |  | 18 | -
D2010.20 – Domestic Water Equipment | [6 empty] | 300 |  |  |  | 300 |  | 18 | Y
D2010.40 – Domestic Water Piping | [6 empty] | 300 |  |  |  | 300 |  | 18 | Y (C,D)
D2010.60 – Plumbing Fixtures | [6 empty] | 300 |  |  |  | 300 |  | 18 | Y (E)
D2010.90 – Domestic Water Distribution Supplementary Components | [6 empty] | 300 |  |  |  | 300 |  | 11 | Y (CC)
D2020 – Sanitary Drainage
D2020.10 – Sanitary Sewerage Equipment | [6 empty] | 300 |  |  |  | 300 |  | 18 | Y (C)
D2020.30 – Sanitary Sewerage Piping | [6 empty] | 300 |  |  |  | 300 |  | 18 | Y (DD)
D2020.90 – Sanitary Drainage Supplementary Components | [6 empty] | 300 |  |  |  | 300 |  | 11 | Y (CC)
D2030 – Building Support Plumbing Systems
D2030.10 – Stormwater Drainage Equipment | [6 empty] | 300 |  |  |  | 300 |  | 18 | Y (C)
D2030.20 – Stormwater Drainage Piping | [6 empty] | 300 |  |  |  | 300 |  | 18 | -
D2030.30 – Facility Stormwater Drains | [6 empty] | 300 |  |  |  | 300 |  | 18 | -
D2030.60 – Gray Water Systems | [6 empty] | 300 |  |  |  | 300 |  | 18 | -
D2030.90 – Building Support Plumbing System Supplementary Components | [6 empty] | 300 |  |  |  | 300 |  | 11 | -
D2050 – General Service Compressed-Air | [6 empty] | 300 |  |  |  | 300 |  |  | -
D2060 – Process Support Plumbing Systems
D2060.10 – Compressed-Air Systems | [6 empty] | 300 |  |  |  | 300 |  | 18 | Y (F)
D2060.20 – Vacuum Systems | [6 empty] | 300 |  |  |  | 300 |  | 18 | -
D2060.30 – Gas Systems | [6 empty] | 300 |  |  |  | 300 |  | 18 | -
D2060.40 – Chemical-Waste Systems | [6 empty] | 300 |  |  |  | 300 |  | 18 | -
D2060.50 – Processed Water Systems | [6 empty] | 300 |  |  |  | 300 |  | 18 | -
D2060.90 – Process Support Plumbing System Supplementary Components | [6 empty] | 300 |  |  |  | 300 |  | 11 | -
D30 HVAC
D3010 – Facility Fuel Systems
D3010.10 – Fuel Piping | [6 empty] | 300 |  |  |  | 300 |  | 18 | -
D3010.30 – Fuel Pumps | [6 empty] | 300 |  |  |  | 300 |  | 18 | -
D3010.50 – Fuel Storage Tanks | [6 empty] | 300 |  |  |  | 300 |  | 18 | -
D3020 – Heating Systems
D3020.10 – Heat Generation | [6 empty] | 300 |  |  |  | 300 |  | 17, 18 | Y (C,G,H)
D3020.30 – Thermal Heat Storage | [6 empty] | 300 |  |  |  | 300 |  | 17, 18 | -
D3020.70 – Decentralized Heating Equipment | [6 empty] | 300 |  |  |  | 300 |  | 17, 18 | -
D3020.90 – Heating System Supplementary Components | [12 empty] | 21 | Y (H)
D3030 – Cooling Systems
D3030.10 – Central Cooling | [6 empty] | 300 |  |  |  | 300 |  | 17, 18 | Y (I,J)
D3030.30 – Evaporative Air-Cooling | [6 empty] | 300 |  |  |  | 300 |  | 17, 18 | Y
D3030.50 – Thermal Cooling Storage | [6 empty] | 300 |  |  |  | 300 |  | 17, 18 | -
D3030.70 – Decentralized Cooling | [6 empty] | 300 |  |  |  | 300 |  | 17, 18 | Y (K)
D3030.90 – Cooling System Supplementary Components | [13 empty] | -
D3050 – Facility HVAC Distribution Systems
D3050.10 – Facility Hydronic Distribution | [6 empty] | 300 |  |  |  | 300 |  | 17, 18 | Y (C,J,L)
D3050.30 – Facility Steam Distribution | [6 empty] | 300 |  |  |  | 300 |  | 17, 18 | Y (C,M)
D3050.50 – HVAC Air Distribution | [6 empty] | 300 |  |  |  | 300 |  | 17, 18 | Y (N)
D3050.90 – Facility Distribution Systems Supplementary Components | [13 empty] | -
D3060 – Ventilation
D3060.10 – Supply Air | [6 empty] | 300 |  |  |  | 300 |  | 17 | -
D3060.20 – Return Air | [6 empty] | 300 |  |  |  | 300 |  | 17 | -
D3060.30 – Exhaust Air | [6 empty] | 300 |  |  |  | 300 |  | 17 | Y (O)
D3060.40 – Outside Air | [6 empty] | 300 |  |  |  | 300 |  | 17 | -
D3060.60 – Air-to-Air Energy Recovery | [6 empty] | 300 |  |  |  | 300 |  | 17 | Y
D3060.70 – HVAC Air Cleaning | [6 empty] | 300 |  |  |  | 300 |  | 17 | -
D3060.90 – Ventilation Supplementary Components | [13 empty] | -
D3070 – Special Purpose HVAC System
D3070.10 – Snow Melting | [6 empty] | 200 |  |  |  | 200 |  |  | -
D40 Fire Protection
D4010 – Fire Suppression
D4010.10 – Water-Based Fire-Suppression | [6 empty] | 200 |  |  |  | 200 |  | 4, 18 | Y (P)
D4010.50 – Fire-Extinguishing | [6 empty] | 200 |  |  |  | 200 |  | 4, 18 | -
D4010.90 – Fire Suppression Supplementary Components | [12 empty] | 4 | -
D4030 – Fire Protection Specialties
D4030.10 – Fire Protection Cabinets | [6 empty] | 200 |  |  |  | 200 |  |  | Y (EE)
D4030.30 – Fire Extinguishers | [6 empty] | 200 |  |  |  | 200 |  |  | Y
D4030.50 – Breathing Air Replenishment Systems | [6 empty] | 200 |  |  |  | 200 |  |  | -
D4030.70 – Fire Extinguisher Accessories | [6 empty] | 200 |  |  |  | 200 |  |  | -
D50 Electrical
D5010 – Facility Power Generator
D5010.10 – Packaged Generator Assemblies | [6 empty] | 200 |  |  |  | 300 |  |  | Y (Q)
D5010.20 – Battery Equipment | [6 empty] | 200 |  |  |  | 300 |  |  | Y (R,S)
D5010.30 – Photovoltaic Collectors | [6 empty] | 200 |  |  |  | 300 |  |  | Y (S)
D5010.40 – Fuel Cells | [6 empty] | 200 |  |  |  | 300 |  |  | -
D5010.60 – Power Filtering and Conditioning | [6 empty] | 200 |  |  |  | 300 |  |  | -
D5010.70 – Transfer Switches | [6 empty] | 200 |  |  |  | 300 |  |  | Y
D5010.90 – Facility Power Generation Supplementary Components | [12 empty] | 5 | -
D5020 – Electrical Service and Distribution
D5020.10 – Electrical Service | [6 empty] | 300 |  |  |  | 300 |  |  | Y (T)
D5020.30 – Power Distribution | [6 empty] | 300 |  |  |  | 300 |  | 14 | Y (U)
D5020.70 – Facility Grounding | [12 empty] | 5 | -
D5020.90 – Electrical Service and Distribution Supplementary Components | [12 empty] | 5 | -
D5030 – General Purpose Electrical Power
D5030.10 – Branch Wiring System | [6 empty] | 200 |  |  |  | 200 |  | 6, 14 | -
D5030.50 – Wiring Devices | [6 empty] | 200 |  |  |  | 200 |  |  | -
D5030.90 – General Purpose Electrical Power Supplementary Components | [12 empty] | 5, 14 | -
D5040 – Lighting
D5040.10 – Lighting Control | [6 empty] | 200 |  |  |  | 200 |  |  | Y (U)
D5040.20 – Branch Wiring for Lighting | [6 empty] | 200 |  |  |  | 200 |  | 6, 14 | -
D5040.50 – Lighting Fixtures | [6 empty] | 300 |  |  |  | 300 |  |  | Y (AA)
D5040.90 – Lighting Supplementary Components | [12 empty] | 5 | -
D5080 – Miscellaneous Electrical Systems
D5080.10 – Lightning Protection | [12 empty] | 7 | -
D5080.40 – Cathodic Protection | [12 empty] | 5 | -
D5080.70 – Transient Voltage Suppression | [12 empty] | 5 | -
D5080.90 – Miscellaneous Electrical Systems Supplementary Components | [12 empty] | 5 | -
D60 Communications
D6010 – Data Communications
D6010.10 – Data communications Network Equipment | [6 empty] | 200 |  |  |  | 200 |  | 19 | -
D6010.20 – Data Communications Hardware | [6 empty] | 200 |  |  |  | 200 |  | 19 | -
D6010.30 – Data communications Peripheral Data Equipment | [6 empty] | 200 |  |  |  | 200 |  | 19 | -
D6010.50 – Data Communications Software | [12 empty] | 19 | -
D6010.60 – Data Communication Program and Integration Services | [13 empty] | -
D6020 – Voice Communications
D6020.10 – Voice Communications Switching and Routing Equipment | [6 empty] | 300 |  |  |  | 300 |  | 19 | -
D6020.20 – Voice Communications Terminal Equipment | [12 empty] | 19 | -
D6020.30 – Voice Communications Messaging | [12 empty] | 19 | -
D6020.40 – Call Accounting | [12 empty] | 19 | -
D6020.50 – Call Management | [6 empty] | 200 |  |  |  | 200 |  | 19 | -
D6030 – Audio-Video Communications
D6030.10 – Audio-Video Systems | [6 empty] | 200 |  |  |  | 200 |  | 19 | -
D6030.50 – Electronic Digital Systems | [6 empty] | 200 |  |  |  | 200 |  | 19 | -
D6060 – Distributed Communications and Monitoring
D6060.10 – Distributed Audio-Video Communications Systems | [6 empty] | 200 |  |  |  | 200 |  | 19 | -
D6060.30 – Healthcare Communications and Monitoring | [6 empty] | 200 |  |  |  | 200 |  | 19 | -
D6060.50 – Distributed Systems | [6 empty] | 200 |  |  |  | 200 |  |  | -
D6090 – Communications Supplementary Components
D6090.10 – Supplementary Components | [6 empty] | 200 |  |  |  | 200 |  | 13 | -
D70 Electronic Safety and Security
D7010 – Access Control and Intrusion Detection
D7010.10 – Access Control | [6 empty] | 200 |  |  |  | 200 |  | 20 | -
D7010.50 – Intrusion Detection | [6 empty] | 200 |  |  |  | 200 |  | 20 | -
D7030 – Electronic Surveillance
D7030.10 – Video Surveillance | [6 empty] | 200 |  |  |  | 200 |  | 20 | -
D7030.50 – Electronic Personal Protection | [6 empty] | 200 |  |  |  | 200 |  | 20 | Y (V)
D7050 – Detection and Alarm
D7050.10 – Fire Detection and Alarm | [6 empty] | 300 |  |  |  | 300 |  | 20 | Y (W)
D7050.20 – Radiation Detection and Alarm | [6 empty] | 300 |  |  |  | 300 |  | 20 | -
D7050.30 – Fuel-Gas Detection and Alarm | [6 empty] | 300 |  |  |  | 300 |  | 20 | -
D7050.40 – Fuel-Oil Detection and Alarm | [6 empty] | 300 |  |  |  | 300 |  | 20 | -
D7050.50 – Refrigeration Detection and Alarm | [6 empty] | 300 |  |  |  | 300 |  | 20 | -
D7050.60 – Water Intrusion Detection and Alarm | [6 empty] | 300 |  |  |  | 300 |  | 20 | -
D7070 – Electronic Monitoring and Control
D7070.10 – Electronic Detention Monitoring and Control | [6 empty] | 200 |  |  |  | 200 |  | 20 | -
D7090 – Electronic Safety and Security Supplementary Components
D7090.10 – Supplementary Components | [6 empty] | 200 |  |  |  | 200 |  | 13 | -
D80 Integrated Automation
D8010 – Integrated Automation Facility Controls
D8010.10 – Integrated Automation Control of Equipment | [13 empty] | -
D8010.20 – Integrated Automation Control of Conveying Equipment | [13 empty] | -
D8010.30 – Integrated Automation Control of Fire-Suppression Systems | [13 empty] | -
D8010.40 – Integrated Automation Control of Plumbing Systems | [13 empty] | -
D8010.50 – Integrated Automation Control of HVAC Systems | [13 empty] | -
D8010.60 – Integrated Automation Control of Electrical Systems | [13 empty] | -
D8010.70 – Integrated Automation Control of Communication Systems | [13 empty] | -
D8010.80 – Integrated Automation Control of Electronic Safety and Security Systems | [13 empty] | -
D8010.90 – Integrated Automation Supplementary Components | [12 empty] | 13 | -
E: Equipment & Furnishings
E10 Equipment
E1010 – Vehicle and Pedestrian Equipment
E1010.10 – Vehicle Servicing Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1010.30 – Interior Parking Control Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1010.50 – Loading Dock Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1010.70 – Interior Pedestrian Control Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1030 – Commercial Equipment
E1030.10 – Mercantile and Service Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1030.20 – Vault Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1030.25 – Teller and Service Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1030.30 – Refrigerated Display Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1030.35 – Commercial Laundry and Dry Cleaning Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1030.40 – Maintenance Equipment | [13 empty] | -
E1030.50 – Hospitality Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1030.55 – Unit Kitchens | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1030.60 – Photographic Processing Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1030.70 – Postal, Packaging, and Shipping Equipment | [13 empty] | -
E1030.75 – Office Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1030.80 – Foodservice Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | Y (X)
E1040 – Institutional Equipment
E1040.10 – Educational and Scientific Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1040.20 – Healthcare Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1040.40 – Religious Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1040.60 – Security Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1040.70 – Detention Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1060 – Residential Equipment
E1060.10 – Residential Appliances | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1060.50 – Retractable Stairs | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1060.70 – Residential Ceiling Fans | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1070 – Entertainment and Recreational Equipment
E1070.10 – Theater and Stage Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1070.20 – Musical Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1070.50 – Athletic Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1070.60 – Recreational Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1090 – Other Equipment
E1090.10 – Solid Waste Handling Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1090.30 – Agricultural Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1090.40 – Horticultural Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
E1090.60 – Decontamination Equipment | [6 empty] | 200 |  |  |  | 200 |  |  | -
E20 Furnishings
E2010 – Fixed Furnishings
E2010.10 – Fixed Art | [6 empty] | 200 |  |  |  | 200 |  |  | -
E2010.20 – Window Treatments | [6 empty] | 200 |  |  |  | 200 |  |  | -
E2010.30 – Casework | [6 empty] | 300 |  |  |  | 300 |  |  | -
E2010.70 – Fixed Multiple Seating | [6 empty] | 200 |  |  |  | 200 |  |  | -
E2010.90 – Other Fixed Furnishings | [6 empty] | 200 |  |  |  | 200 |  |  | -
E2050 – Movable Furnishings
E2050.10 – Movable Art | [6 empty] | 200 |  |  |  | 200 |  |  | -
E2050.30 - Furniture | [6 empty] | 200 |  |  |  | 200 |  |  | -
E2050.40 – Accessories | [6 empty] | 200 |  |  |  | 200 |  |  | -
E2050.60 – Movable Multiple Seating | [6 empty] | 200 |  |  |  | 200 |  |  | -
E2050.90 – Other Movable Furnishings | [6 empty] | 200 |  |  |  | 200 |  |  | -
F: Special Construction & Demolition
F10 Special Construction
F1010 – Integrated Construction
F1010.10 – Building Modules | [6 empty] | 300 |  |  |  | 300 |  |  | -
F1010.50 – Manufactured/Fabricated Rooms | [6 empty] | 300 |  |  |  | 300 |  |  | -
F1010.70 – Modular Mezzanines | [6 empty] | 300 |  |  |  | 300 |  |  | -
F1020 – Special Structures
F1020.10 – Fabric Structures | [13 empty] | -
F1020.20 – Space Frames | [13 empty] | -
F1020.30 – Geodesic Structures | [13 empty] | -
F1020.40 – Manufacturer-engineered Structures | [13 empty] | -
F1020.60 – Manufactured Canopies | [13 empty] | -
F1020.65 – Rammed Earth Construction | [13 empty] | -
F1020.70 – Towers | [13 empty] | -
F1030 – Special Function Construction
F1030.10 – Sound and Vibration Control | [13 empty] | -
F1030.30 – Seismic Control | [13 empty] | -
F1030.50 – Radiation Protection | [13 empty] | -
F1050 – Special Facility Components
F1050.10 – Pools | [6 empty] | 300 |  |  |  | 300 |  |  | -
F1050.20 – Interior Fountains | [6 empty] | 200 |  |  |  | 200 |  |  | -
F1050.30 – Interior Water Features | [6 empty] | 200 |  |  |  | 200 |  |  | -
F1050.40 – Aquariums | [6 empty] | 200 |  |  |  | 200 |  |  | -
F1050.50 – Amusement Park Structures and Equipment | [13 empty] | -
F1050.60 – Ice Rinks | [6 empty] | 200 |  |  |  | 200 |  |  | -
F1050.70 – Animal Containment | [6 empty] | 200 |  |  |  | 200 |  |  | -
F1060 – Athletic and Recreational Special Construction
F1060.10 – Indoor Soccer Boards | [6 empty] | 200 |  |  |  | 200 |  |  | -
F1060.20 – Safety Netting | [6 empty] | 200 |  |  |  | 200 |  |  | -
F1060.30 – Arena Football Boards | [6 empty] | 200 |  |  |  | 200 |  |  | -
F1060.40 – Floor Sockets | [6 empty] | 200 |  |  |  | 200 |  |  | -
F1060.50 – Athletic and Recreational Court Walls | [6 empty] | 200 |  |  |  | 200 |  |  | -
F1060.60 – Demountable Athletic Surfaces | [6 empty] | 200 |  |  |  | 200 |  |  | -
F1080 – Special Instrumentation
F1080.10 – Stress Instrumentation | [13 empty] | -
F1080.20 – Seismic Instrumentation | [13 empty] | -
F1080.40 – Meteorological Instrumentation | [13 empty] | -
F1080.60 – Earth Movement Monitoring | [13 empty] | -
F20 Facility Remediation
F2010 – Hazardous Materials Remediation
F2010.10 – Transportation and Disposal of Hazardous Materials | [13 empty] | -
F2010.20 – Asbestos Remediation | [13 empty] | -
F2010.30 – Lead Remediation | [13 empty] | -
F2010.40 – Polychlorinate Biphenyl Remediation | [13 empty] | -
F2010.50 – Mold Remediation | [13 empty] | -
F30 Demolition
F3010 – Structure Demolition
F3010.10 – Building Demolition | [6 empty] | 200 | [6 empty] | -
F3010.30 – Tower Demolition | [13 empty] | -
F3010.50 – Bridge Demolition | [13 empty] | -
F3010.70 – Dam Demolition | [13 empty] | -
F3030 – Selective Demolition
F3030.10 – Selective Building Demolition | [6 empty] | 200 | [6 empty] | -
F3030.30 – Selective Interior Demolition | [6 empty] | 200 | [6 empty] | -
F3030.50 – Selective Bridge Demolition | [13 empty] | -
F3030.70 – Selective Historic Demolition | [13 empty] | -
F3050 – Structure Moving
F3050.10 – Structure Relocation | [6 empty] | 300 |  |  |  | 300 |  |  | -
F3050.30 – Structure Raising | [6 empty] | 300 |  |  |  | 300 |  |  | -
G: Building Sitework
G10 Site Preparation
G1010 – Site Clearing
G1010.10 – Clearing and Grubbing | [13 empty] | -
G1010.30 – Tree and Shrub Removal and Trimming | [13 empty] | -
G1010.50 – Earth Stripping and Stockpiling | [13 empty] | -
G1020 – Site Elements Demolition
G1020.10 – Utility Demolition | [12 empty] | 9 | -
G1020.30 – Infrastructure Demolition | [12 empty] | 9 | -
G1020.50 – Selective Site Demolition | [12 empty] | 9 | -
G1030 – Site Element Relocation
G1030.10 – Utility Relocation | [12 empty] | 9 | -
G1050 – Site Remediation
G1050.10 – Physical Decontamination | [13 empty] | -
G1050.15 – Chemical Decontamination | [13 empty] | -
G1050.20 – Thermal Decontamination | [13 empty] | -
G1050.25 – Biological Decontamination | [13 empty] | -
G1050.30 – Remediation Soil Stabilization | [13 empty] | -
G1050.40 – Site Containment | [13 empty] | -
G1050.45 – Sinkhole Remediation | [13 empty] | -
G1050.50 – Hazardous Waste Drum Handling | [13 empty] | -
G1050.80 – Water Remediation | [13 empty] | -
G1070 – Site Earthwork
G1070.10 – Grading | [12 empty] | 9 | -
G1070.20 – Excavation and Fill | [12 empty] | 9 | -
G1070.30 – Embankments | [12 empty] | 9 | -
G1070.35 – Erosion and Sedimentation Controls | [12 empty] | 9 | -
G1070.40 – Soil Stabilization | [12 empty] | 9 | -
G1070.45 – Rock Stabilization | [12 empty] | 9 | -
G1070.50 – Soil Reinforcement | [12 empty] | 9 | -
G1070.55 – Slope Protection | [12 empty] | 9 | -
G1070.60 – Gabions | [12 empty] | 9 | -
G1070.65 – Riprap | [12 empty] | 9 | -
G1070.70 – Wetlands | [12 empty] | 9 | -
G1070.80 – Earth Dams | [12 empty] | 9 | -
G1070.90 – Site Soil Treatment | [12 empty] | 9 | -
G20 Site Improvements
G2010 – Roadways
G2010.10 – Roadway Pavement | [12 empty] | 9 | -
G2010.20 – Roadway Curbs and Gutters | [12 empty] | 9 | -
G2010.40 – Roadway Appurtenances | [12 empty] | 9 | -
G2010.70 – Roadway Lighting | [12 empty] | 9 | -
G2010.80 – Vehicle Fare Collection | [12 empty] | 9 | -
G2020 – Parking Lots
G2020.10 – Parking Lot Pavement | [12 empty] | 9 | -
G2020.20 – Parking Lot Curbs and Gutters | [12 empty] | 9 | -
G2020.40 – Parking Lot Appurtenances | [6 empty] | 300 |  |  |  | 300 |  | 9, 23 | -
G2020.70 – Parking Lot Lighting | [6 empty] | 300 |  |  |  | 300 |  | 9, 21 | Y(Z)
G2020.80 – Exterior Parking Control Equipment | [12 empty] | 9 | -
G2030 – Pedestrian Plazas and Walkways
G2030.10 – Pedestrian Pavement | [12 empty] | 9 | -
G2030.20 – Pedestrian Pavement Curbs and Gutters | [12 empty] | 9 | -
G2030.30 – Exterior Steps and Ramps | [12 empty] | 9 | -
G2030.40 – Pedestrian Pavement Appurtenances | [12 empty] | 9 | -
G2030.70 – Plaza and Walkway Lighting | [12 empty] | 9 | -
G2030.80 – Exterior Pedestrian Control Equipment | [12 empty] | 9 | -
G2040 – Airfields
G2040.10 – Aviation Pavement | [13 empty] | -
G2040.20 – Aviation Pavement Curbs and Gutters | [13 empty] | -
G2040.40 – Aviation Pavement Appurtenances | [13 empty] | -
G2040.70 – Airfield Lighting | [13 empty] | -
G2040.80 – Airfield Signaling and Control Equipment | [13 empty] | -
G2050 – Athletic, Recreational, and Playfield Areas
G2050.10 – Athletic Areas | [12 empty] | 9 | -
G2050.30 – Recreational Areas | [12 empty] | 9 | -
G2050.50 – Playfield Areas | [12 empty] | 9 | -
G2060 – Site Development
G2060.10 – Exterior Fountains | [12 empty] | 9 | -
G2060.20 – Fences and Gates | [12 empty] | 9 | -
G2060.25 – Site Furnishings | [12 empty] | 9 | -
G2060.30 – Exterior Signage | [12 empty] | 9 | -
G2060.35 – Flagpoles | [12 empty] | 9 | -
G2060.40 – Covers and Shelters | [12 empty] | 9 | -
G2060.45 – Exterior Gas Lighting | [12 empty] | 9 | -
G2060.50 – Site Equipment | [12 empty] | 9 | -
G2060.60 – Retaining Walls | [12 empty] | 9 | -
G2060.70 – Site Bridges | [12 empty] | 9 | -
G2060.80 – Site Screening Devices | [12 empty] | 9 | -
G2060.85 – Site Specialties | [12 empty] | 9 | -
G2080 – Landscaping
G2080.10 – Planting Irrigation | [12 empty] | 9 | -
G2080.20 – Turf and Grasses | [12 empty] | 9 | -
G2080.30 – Plants | [12 empty] | 9 | -
G2080.50 – Planting Accessories | [12 empty] | 9 | -
G2080.70 – Landscape Lighting | [12 empty] | 9 | -
G2080.80 – Landscape Activities | [12 empty] | 9 | -
G30 Liquid and Gas Site Utilities
G3010 – Water Utilities
G3010.10 – Site Domestic Water Distribution | [6 empty] | 300 |  |  |  | 300 |  | 12, 21 | Y (BB)
G3010.30 – Site Fire Protection Water Distribution | [6 empty] | 300 |  |  |  | 300 |  | 12, 21 | -
G3010.50 – Site Irrigation Water Distribution | [12 empty] | 12 | -
G3020 – Sanitary Sewerage Utilities
G3020.10 – Sanitary Sewerage Utility Connection | [12 empty] | 12 | -
G3020.20 – Sanitary Sewerage Piping | [12 empty] | 12 | -
G3020.40 – Utility Septic Tanks | [12 empty] | 12 | -
G3020.50 – Sanitary Sewerage Structures | [12 empty] | 12 | -
G3020.60 – Sanitary Sewerage Lagoons | [12 empty] | 12 | -
G3030 – Storm Drainage Utilities
G3030.10 – Storm Drainage Utility Connection | [12 empty] | 12 | -
G3030.20 – Storm Drainage Piping | [12 empty] | 12 | -
G3030.30 – Culverts | [12 empty] | 12 | -
G3030.40 – Site Storm Water Drains | [12 empty] | 12 | -
G3030.50 – Storm Drainage Pumps | [12 empty] | 12 | -
G3030.60 – Site Subdrainage | [12 empty] | 12 | -
G3030.70 – Storm Drainage Ponds and Reservoirs | [12 empty] | 12 | -
G3050 – Site Energy Distribution
G3050.10 – Site Hydronic Heating Distribution | [12 empty] | 12 | -
G3050.20 – Site Steam Energy Distribution | [6 empty] | 300 |  |  |  | 300 |  | 12, 21 | Y (Y)
G3050.40 – Site Hydronic Cooling Distribution | [12 empty] | 12 | -
G3060 – Site Fuel Distribution
G3060.10 – Site Gas Distribution | [12 empty] | 12 | -
G3060.20 – Site Fuel-Oil Distribution | [6 empty] | 300 |  |  |  | 300 |  | 12, 21 | -
G3060.30 – Site Gasoline Distribution | [12 empty] | 12 | -
G3060.40 – Site Diesel Fuel Distribution | [12 empty] | 12 | -
G3060.60 – Site Aviation Fuel Distribution | [12 empty] | 12 | -
G3090 – Liquid and Gas Site Utilities Supplementary Components | [12 empty] | 12 | -
G3090.10 – Supplementary Components | [12 empty] | 12 | -
G40 Electrical Site Improvements
G4010 – Site Electric Distribution Systems
G4010.10 – Electrical Utility Services | [6 empty] | 300 |  |  |  | 300 |  | 10, 21 | -
G4010.20 – Electric Transmission and Distribution | [12 empty] | 10 | -
G4010.30 – Electrical Substations | [12 empty] | 10 | -
G4010.40 – Electrical Transformers | [12 empty] | 10 | -
G4010.50 – Electrical Switchgear and Protection Devices | [12 empty] | 10 | -
G4010.70 – Site Grounding | [13 empty] | -
G4010.90 – Electrical Distribution System Instrumentation | [13 empty] | -
G4050 – Site Lighting
G4050.10 – Area Lighting | [6 empty] | 300 |  |  |  | 300 |  | 21 | Y (Z)
G4050.20 – Flood Lighting | [13 empty] | -
G4050.50 – Building Illumination | [13 empty] | -
G4050.90 – Exterior Lighting Supplementary Components | [13 empty] | -
G50 Site Communications
G5010 – Site Communications Systems
G5010.10 – Site Communications Structures | [13 empty] | -
G5010.30 – Site Communications Distribution | [13 empty] | -
G5010.50 – Wireless Communications Distribution | [13 empty] | -
G90 Miscellaneous Site Construction
G9010 - Tunnels
G9010.10 – Vehicular Tunnels | [6 empty] | 300 |  |  |  | 300 |  |  | -
G9010.20 – Pedestrian Tunnels | [6 empty] | 300 |  |  |  | 300 |  |  | -
G9010.40 – Service Tunnels | [6 empty] | 300 |  |  |  | 300 |  |  | -
G9010.90 – Tunnel Construction Related Activities | [13 empty] | -
Note on O2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Not for Use for Wexner Medical Center Projects

## Asset Tag Notes
Asset Tag Notes
Note
A | To include all corridor doors and fire + smoke rated doors (automatic and manual) as well as overhead and rolling fire doors. To include all other doors/access openings (such as utility access doors) in rated assemblies.
B | To include only overhead electric door openers
C | To include only pumps, sump pumps and sewage ejector pumps
D | To include only backflow preventers and domestic water shutoffs
E | To include only emergency showers/eyewash stations and combos, surgical sinks, safety equipment, and water coolers/fountains
F | To include only air compressors, medical air compressors, air dryers, and air receiver tanks
G | To include only boilers, radiant gas heaters, steam generators, and deaerators
H | To include only shell & tube heat exchangers
I | To include only chillers, condensers, cooling towers, packaged HVAC units, expansion tanks and water softeners
J | To include only water treatment/softeners
K | To include heat pumps, plate & frame heat exchangers, split system and portable AC units (through the wall unit, window unit, etc.)
L | To include deaerators, expansion tanks, and shot feeders
M | To include only steam traps, condensate return units, and high pressure steam shutoffs
N | To include air curtains, air handling units, fans, V.A.V./mixing boxes, humidifiers and dampers (fire, smoke, fire/smoke, control). Dampers spanning multiple rooms should be associated with the room in which the technician would enter to access/service the damper. Damper access panel location to be confirmed by the contractor, and update room associations accordingly
O | To include only fumehoods
P | To include only fire pumps, and fire system air compressors
Q | To include only emergency generators, diesel and natural gas generators
R | To include only uninterrupted power supplies
S | To include only Inverters and PV Arrays
T | To include only oil filled and dry transformers
U | To include only electric panelboards, distribution panels, lighting control panels, main switchboards, variable frequency drives, and motor control centers
V | To include only emergency phones & poles
W | To include only pull stations and fire alarm panels
X | To include only ice machines
Y | To include only desuperheaters
Z | To include only pole lights and parking lot lights
AA | To include battery powered lights, and all exit lights and emergency egress lights (i.e. battery and non-battery powered exit/emergency egress light), as well as lights on the emergency circuit/backup generator.
BB | To include only hydrants
CC | To include plumbing valves for the building main line and major branch lines from the main (e.g. floor distribution). To include inline strainers (e.g. Y strainer)
DD | To include only grease interceptors
EE | To include only mechanically vented.